## Slide 1
Next Generation Communication Server
CS1000
2003.08
Installation and Upgrade

## Slide 2
Installation Process
HW Install
RS232C
Connection
to PC
Emulator
Execution
in PC
System
Power On
Login ID &
Password
Input
DiskOnChip
Format
Off Line Mode
By Ctrl-Z
OMS Install
in PC
CPM.IMG
Upload
FTP Tool
CPM Restart
OMS
Reconnect
System Setup
Information Set
Menu 1.1
Press
Sys Init. Icon
Menu 2.2
Holiday Set by
Automatic
pop-up Menu
Number Plan
Set by Automatic
Pop-up Menu
Local Board
Data Set
Menu 2.2
Trunk Access
Code Set
Menu 4.2
IC Digit Remove
Count Set
Menu 4.3
Others Data
Set
each Menu
Make Data File
Mouse R-Button
Back-Up
CS1000.DT
FTP Tool
Network
Configuration
Trunk Outgoing
Group Set
Menu 4.2
Verify
CPM Restarting
via SIO
Verify the file size
Set Network Sync.
Site History Update
History Manage Tool

## Slide 3
Upgrade Process
OMS
Connect
Delete cpm.img
FTP Tool
Upload cpm.img
FTP Tool
Check func.dt
compatibility
X change ?
Make Data File
Mouse R-Button
Delete pmstx.dq
FTP Tool
Delete func.dt
FTP Tool
Make upgrade.dt
Mouse R-Button
Apply upgrade.dt
Mouse R-Button
Verify the file size
Is there any special
NOTICE for this version ?
I must check
the release notice information
to know what is different from
previous version.
New OMS
Install
Check
Version Release
Notice
Site History Update
History Manage Tool
FW Status Check
Version Check Tool
CPM Restart
Upgrade(v3.20Xx or below -> v3.25 or above

## Slide 4
CPM Memory Description
Boot PROM 4 M bit : Monitor Program for Off Line Mode
Tone PROM 4 M bit : Call Processing Tone Resource + DTMF Resource
DRAM 16 M byte : OS + S/W + User Data Base + Working Data Base + Stack
DiskOnChip 8M byte or 16M byte with File System
: All System Files
NVRAM in Clock Chip 50 byte : Network Configure Information
SRAM 0 M byte

## Slide 5
System Files
Data File
- cs1000.dt : back up file for data generated by OMS manually. (numbering plan, LCR, speed code..)
- func.dt : back up file for data generated by user automatically when the user uses some feature.
(call forward, wake up, message wait….)
- dconf.dt : back up file for data generated in part of OMS diagnosis manually.
- acdgen.dt : back up file for data generated by ACD Manager manually. (CCV, agent info…)
- speed.dt : special back up file for only speed code.
- lcr.dt : special back up file for only LCR info.
- upgrade.dt : back up file for all kind of data in func.dt. (will include flex.dt)
Disk Queue Files
- fault.dq : system fault message queue for communication with OMS.
- netft.dq : slave system fault message queue for communication with OMS.(Centralized Alarm)
- pmxtx.dq : PMS TX message queue for HOTEL Service and SMDA.
- smda2.dq : Duplicated SMDA TX message queue.
Others
- config.sys : system initial configuration file for VMS, SMDA, ANI info…

## Slide 6
$ dir
Volume in drive DiskOnChip has no label
Volume Serial Number is none
Directory of DiskOnChip:\
cpm.img 3560592 01-31-2002 17:23:16
pmstx.dq 1000016 01-31-2002 17:26:16
fault.dq 2416 02-01-2002 17:44:08
func.dt 932989 02-01-2002 17:03:15
dconf.dt 2096 02-01-2002 17:46:02
cs1000.dt 59626 02-01-2002 10:30:19
6 file(s) 5557735 bytes
0 dir(s) 2562048 bytes free
Total = about 8M byte
DiskOnChip (8M)

## Slide 7
$ dir
Volume in drive DiskOnChip has no label
Volume Serial Number is none
Directory of DiskOnChip:\
cpm.img 4709808 12-08-2003 17:13:12
cs1000.dt 98749 12-08-2003 17:19:05
pmstx.dq 2400016 12-23-2003 14:08:20
fault.dq 2416 12-29-2003 10:56:00
netft.dq 28016 12-22-2003 15:22:23
smda2.dq 2400016 11-15-2003 10:32:17
func.dt 933228 12-23-2003 17:32:20
dconf.dt 2096 12-23-2003 14:08:31
config.sys 22 11-15-2003 11:05:23
9 file(s) 10574367 bytes
0 dir(s) 5724160 bytes free
Total = about 16M byte
DiskOnChip (16M)

## Slide 8
FTP Manager

## Slide 9
System Initial Process
CPM restart
OS load to RAM
Cpm.img load to RAM
Config.sys read
Dconf.dt read or creation(*)
Fault.dq creation or not(*)
Pmstx.dq creation or not(*)
Smda2.dq creation or not(*)
Protection Data Base Initial
CS1000.DT exit ?
Read CS1000.DT
Protection Data Base update
Working Data Base Initial
CS1000.DT exit ?
Read FUNC.DT
Working Data Base update
Delete FUNC.DT
Create FUNC.DT
FUNC.DT exit ?
Call Main() Start
YES
YES
YES
ACDGEN.DT exit ?
Read CS1000.DT
ACD Data Base update

## Slide 10
SIO and LAN port usage
CPM have 1 LAN(10 base T) port and 4 SIO ports.
Default 4 SIO ports usage
1st port(IOT 1) on left panel : for system monitoring
2nd port(IOT 2) on left panel : for external VMS
3rd port(CN 4) on IOTU : for PMS/SMDA
A user can assign the SIO ports and LAN port for other service by followed procedure.
1) connect OMS to CPM.
2) go to CONFIG menu.
3) select the menu 1.10 Config File Maker
4) make configuration
5) save the configuration to file by save button(config.sys)
6) execute the FTP File Manager in Tool menu
7) connect to CPM
8) upload the config.sys file
9) disconnect the FTP File Manager
10) close the FTP File Manager
11) restart CPM
If there is any config.sys file,
all default usage of SIO will be ignored.

## Slide 11
Off Line Data Generation(Virtual CS1000)
A system manager can generate the customer data
in his office even through he don’t have the system.

## Slide 12
Network Synchronization Rule
Singular Sync. Master Use Case
During CPM uses the outside clock from the pre assigned local board, if the local board reports Sync-fail
to CPM, the local board will receive the Sync. Slave command from CPM and CPM will use own clock
immediately.
During CPM uses own clock, if the Board reports Sync-recover to CPM, CPM will wait about 7secs.
For the time, if the local board don’t report Sync-fail to CPM any more, the local board will receive the
Sync. Master command from CPM and CPM will use the outside clock from the local board.
Plural Sync. Master Use Case
During CPM uses the outside clock from the local board having the first priority, if the local board reports
Sync-fail to CPM, the local board will receive the Sync. Slave command from CPM immediately and the
local board having the second priority will receive the Sync. Master command in 5secs and CPM will use
the outside clock from the new master local board immediately.
During CPM uses the outside clock from the new master local board, if the local board having the first
priority reports Sync-recover to CPM, CPM will wait about 30secs.
For the time, if the local board don’t report Sync-fail to CPM any more, the local board will receive the
Sync. Master command from CPM and the local board having the second priority receive at the same
time. And the CPM will use the outside clock from the local board having the first priority.

## Slide 13
CPM Duplication 1
Precondition to make the activation of the duplication :
1) both CPM should have same IP address and MAC address.
2) the system should have CS1000.DT.
3) After the standby CPM inserts, should wait about one minute until the standby CPM reads
the CS1000.DT and FUNC.DT. Also you should do when you orders the make_seed to CPM
by OMS.
When the standby CPM completes to read the data seed files, you will see the change of the
status LED in front of CPM.
Range :
just only 1st conversation.
Notices :
1) If you want to restart the system having CPM duplication, you should press not the standby CPM
reset button but the active CPM reset button.
2) If you want to discard the active CPM, you should push the disk access stick in front of CPM
to the disable status direction.

## Slide 14
CPM Duplication 2
Inject
the 1st CPM
Preparing process of the the duplication :
Power On
the system
Connect
SIO to system
Login ID &
Password
Input
Set
IP&MAC address
Wait….
Press the reset button
of the active CPM
Inject
the 2nd CPM
Wait….
Set
IP&MAC address
Press the reset button
of the active CPM
Wait….
* Wait…. : Until the status LED of the restarting CPM moves from
top to bottom.

## Slide 15
System Day/Night Mode
Automatic Day/Night Mode Change
1) by Night Bar
Should set the Night Bar Use Option in OMS Menu 16.3 Night Bar
2) by ATD Night Button
Should reset the Night Bar Use Option in OMS Menu 16.3 Night Bar
Manual Day/Night Mode Change
1) by feature code of ATD
Day Mode Set : Admin + 4 + 0
Night Mode Set : Admin + 4 + 1
2) by feature code of predefined extension
Day Mode Set : *62
Night Mode Set : *61
Verify the system Mode in LCD of ATD

## Slide 16
Incoming Digit Modification 1
Digit Remove
Digit Change
Flexible DDI

## Slide 17
Incoming Digit Modification 2
Digit Remove
Digit Change
Flexible DDI

## Slide 18
Incoming Digit Modification 3
Digit Remove
Digit Change
Flexible DDI